## Feuil1
Calculation of the solar PV energy ouput of a photovoltaic system
Yelow cell = enter your own data
Green cell = result (do not change the value)
White cell = calculated value (do not change the value)
Global formula : |  | E = A * r * H * PR
E = Energy (kWh) |  |  |  |  | 2810.7914 | kWh/an
A = Total solar panel Area (m²) |  |  |  |  | 20 | m²
r = solar panel yield (%) |  |  |  |  | 15%
H = Annual average irradiation on tilted panels (shadings not included)* |  |  |  |  | 1250 | kWh/m².an
PR = Performance ratio, coefficient for losses (range between 0.9 and 0.5, default value = 0.75) |  |  |  |  | 0.74954
|  |  |  | Total power of the system | 3 | kWp
Losses details (depend of site, technology, and sizing of the system)
- | Inverter losses (6% to 15 %) |  |  |  | 8%
- | Température losses (5% to 15%) |  |  |  | 8%
- | DC cables losses (1 to 3 %) |  |  |  | 2%
- | AC cables losses (1 to 3 %) |  |  |  | 2%
- | Shadings 0 % to 40% (depends of site) |  |  |  | 3%
- | Losses weak irradiation 3% yo 7% |  |  |  | 3%
- | Losses due to dust, snow... (2%) |  |  |  | 2%
- | Other Losses |  |  |  | 0%
*You can find this value on the map below or here : |  |  | solar radiation data
You have to find the global annual irradiation incident on your PV panels with your specific inclination (slope, tilt)
and orientation (azimut).
More info Source : www.photovoltaic-software.com